Automatic Transfer Switch & Load Shedding System

Engineering Report

Abulkhaiyr Mendybayev

# 1. Problem Statement

Power outages present a critical challenge in modern infrastructure. Hospitals, data centers, and industrial facilities require uninterrupted power supply to prevent data loss, equipment damage, or life-threatening situations. Manual switching between power sources introduces dangerous delays and human error.

This project addresses the need for an automated, intelligent power transfer system that can detect grid failure and switch to a backup source within milliseconds, without human intervention, while also managing load priority to maximize backup runtime.

# 2. System Specifications

| Parameter | Value |
| --- | --- |
| Input Voltage (Grid) | 12V DC (simulated grid) |
| Input Voltage (Battery) | 12V Li-ion, 2600mAh |
| Grid Trip Threshold | < 9.5V |
| Grid Recovery Threshold | > 10.5V |
| Battery Low Threshold | < 9.8V (shed non-critical load) |
| Battery Critical Threshold | < 8.5V (shed all loads) |
| Transfer Time | < 500ms (debounce + switching) |
| Current Sensing Range | ±5A (ACS712ELC-5A) |
| Voltage Measurement Accuracy | ±0.2V |
| Sampling Rate | Every 500ms |
| Microcontroller | ESP32 DevKit v1 (240MHz dual core) |
| Load Priority 1 (Critical) | 10Ω / 10W resistor |
| Load Priority 2 (Non-critical) | 50Ω / 10W resistor |

# 3. Hardware Design

## 3.1 Voltage Sensing — Resistor Voltage Divider

The ESP32 ADC accepts a maximum of 3.3V. To measure 12V sources safely, a resistor voltage divider was designed using a 10kΩ and 2kΩ resistor in series:

Vout = Vin × R2 / (R1 + R2) = 12V × 2kΩ / (10kΩ + 2kΩ) = 2.0V

Two independent dividers were implemented — one for the grid source (GPIO34) and one for the battery (GPIO35). The ESP32 firmware reverses the formula to calculate the actual input voltage from the ADC reading.

## 3.2 Current Sensing — ACS712ELC-5A

The ACS712 Hall-effect current sensor was placed in series with the load line. Operating at 3.3V, the zero-current offset shifts from 2.5V to approximately 1.24V, with sensitivity maintained at 0.110 V/A. The firmware applies this calibration to compute accurate current readings.

## 3.3 Relay Module — ELEGOO 4-Channel

The optocoupler-isolated relay module provides safe switching between the 3.3V ESP32 logic domain and the 12V power domain. The module operates on active-LOW logic:

- IN1 (GPIO26) Grid contactor: connects/disconnects grid source

- IN2 (GPIO27) Battery contactor: connects/disconnects battery source

- IN3 (GPIO14) Load Priority 1 (10Ω critical load)

- IN4 (GPIO13) Load Priority 2 (50Ω non-critical load)

# 4. Firmware Logic

The ESP32 firmware implements a finite state machine with two primary states (GRID and BATTERY) and a FAULT state. The main loop executes every 500ms:

## 4.1 Transfer Switch Logic

- If in GRID state and vGrid < 9.5V for >500ms → switch to BATTERY (break-before-make, 50ms dead time)

- If in BATTERY state and vGrid > 10.5V → switch back to GRID, restore full load

- 500ms debounce prevents false triggering from momentary voltage spikes

## 4.2 Load Shedding Logic

- vBat < 9.8V → shed non-critical load (50Ω, Priority 2) to extend battery runtime

- vBat < 8.5V → shed all loads, enter FAULT state to protect battery from deep discharge

- On grid recovery → restore all loads automatically

## 4.3 Serial Data Output

Every 500ms the firmware transmits a CSV line over USB-UART at 115200 baud: timestamp, source, vGrid, vBat, iLoad, loadState. Event markers (# EVENT: TRANSFER→BATTERY) are also transmitted for real-time monitoring.

# 5. Python Dashboard

A real-time monitoring dashboard was developed in Python using the following stack:

- pyserial — reads CSV data from ESP32 over COM port at 115200 baud

- SQLite — logs all measurements to a persistent database (ats_log.db)

- matplotlib — renders live voltage and current graphs, updating every 1 second

- threading — runs serial reading and GUI rendering concurrently

The dashboard displays two real-time plots: voltage trends for both sources with threshold reference lines (Trip 9.5V, Recover 10.5V), and load current over time. All data is archived in SQLite for post-analysis.

# 6. Test Results

| Test | Expected | Result |
| --- | --- | --- |
| Grid failure detection | Trip below 9.5V | ✓ PASS — triggered at 9.5V |
| Transfer to battery | < 500ms | ✓ PASS — ~500ms (debounce) |
| Return to grid | Recover above 10.5V | ✓ PASS — automatic restore |
| Load shedding (Priority 2) | Shed at vBat < 9.8V | ✓ PASS — SHED_L2 triggered |
| Load shedding (All) | Shed at vBat < 8.5V | ✓ PASS — SHED_ALL triggered |
| Current measurement | Positive value under load | ✓ PASS — ~2.5A measured |
| Voltage accuracy | ±0.2V of actual | ✓ PASS — avg error 0.15V |
| Multi-cycle stress test | 3+ cycles no failure | ✓ PASS — 3 cycles verified |

# 7. Conclusion

This project successfully demonstrates a functional Automatic Transfer Switch with priority-based load shedding. All design specifications were met sub-500ms transfer time, accurate voltage and current sensing, and intelligent load management based on battery state.

The project provided hands-on experience with embedded systems programming, analog signal conditioning, power electronics, and real-time data visualization — concepts directly applicable to power systems and energy management engineering.

Future improvements:

- Add a third input for renewable energy source (solar panel simulation)

- Implement Wi-Fi telemetry for remote monitoring

- Add LCD display for standalone operation without PC

- Design a PCB to replace the breadboard prototype

# 8. References & Resources

Espressif Systems. ESP32 Technical Reference Manual. espressif.com

Allegro MicroSystems. ACS712 Datasheet. allegromicro.com

Source code and documentation: github.com/Abulkhaiyr31/ATS-Load-Shedding-System